## Sheet1
ASHRAE 62.2 Ventilation Calculation (EXISTING)
Ventilation Needed
BR+1 or People X 7.5cfm
|  |  | 6 | 7.5 | 45 | 1
Square ft / 100
|  |  | 1778 | 100 | 17.78 | 2
Automatic | Room
Calculaton | Existing? | Required cfm | Window | Measured Cfm | Deficit
60 | YES | Kitchen (100) | -20 | -20 | 60
30 | YES | Bath 1 (50) | -20 |  | 30
30 | YES | Bath 2 (50) | -20 |  | 30
|  |  | Total Deficit |  | 120
|  |  | Deficit /4 |  | 30 | 3
|  |  | Ventilation Needed |  | 92.78
Infiltration Credit
CFM50 / N-Value
|  |  | 1700 | 23.2 | 73.2759 | A
Square ft x .02
|  |  | 1778 | 0.02 | 35.56 | B
|  |  | Difference (A-B) |  | 37.7159 | C
|  |  | Infiltration Credit |  | 18.8579 | C/2 | N-Values for Infiltration Credit (Saturn Resource Management)
[7 empty] | Washington | W | 1 | 1.5 | 2 | 2.5 | 3
|  |  | Continuous Ventilation to Add |  | 73.9221 |  | Olympia | 0.77 | 25.565 | 22.637 | 20.7652 | 19.4206 | 18.3869
[7 empty] | Seattle | 0.85 | 23.1589 | 20.5064 | 18.8108 | 17.5928 | 16.6564
|  |  | (Needed - Credit) |  |  |  | Spokane | 0.85 | 23.1589 | 20.5064 | 18.8108 | 17.5928 | 16.6564
[7 empty] | Yakima | 0.81 | 24.3025 | 21.5191 | 19.7398 | 18.4616 | 17.4789
ASHRAE 62.2 Ventilation Calculation (FINAL)
Ventilation Needed
|  |  | BR+1 or People X 7.5cfm |  |  |  | COMMENTS:
|  |  | 6 | 7.5 | 45 | 1
Square ft / 100
|  |  | 1778 | 100 | 17.78 | 2
Automatic | Room
Calculaton | Existing? | Required cfm | Window | Measured Cfm | Deficit
80 | YES | Kitchen (100) | -20 |  | 80
-20 | YES | Bath 1 (50) | -20 | -50 | None
None | NO | Bath 2 (50) |  |  | None
|  |  | Total Deficit |  | 80
|  |  | Deficit /4 |  | 20 | 3
|  |  | Ventilation Needed |  | 82.78
Infiltration Credit
CFM50 / N-Value
|  |  | 1000 | 23.2 | 43.1034 | A
Square ft x .02
|  |  | 1778 | 0.02 | 35.56 | B
|  |  | Difference (A-B) |  | 7.5434 | C
|  |  | Infiltration Credit |  | 3.7717 | C/2
|  |  | Continuous Ventilation to Add |  | 79.0083
(Needed - Credit)
Calculate CONTINUOUS Ventilation needed
1) Multiply Greatest of Bedrooms + 1 or Number of People x 7.5cfm
2)Calculate 1 cfm per 100 Sq ft Floor Area.
3) Calculate Spot Ventilation Deficit by taking required ventilation (e.g. Kitchen 100cfm or Bathroom 50cfm) and subtracting 20 cfm if operable window in room and subtracting measured cfm of existing fan. Divide Total Deficit by 4. Add Calculations (1, 2 and 3) to Determine Ventilation Needed.
Calculate Infiltration Credit
A) Calculate Infiltration Credit By taking CFM50 Blower Door Reading and Dividing by N-Value. (See Table Below)
B)Calculate Sq Ft Floor Area and Multiply by .02
IF A is Greater than B, Then take difference (C) and Divide by 2 for Credit
(if A is not greater that B, then there is no credit) Determine Ventilation to Add
Subtract Infiltration Credit from Ventilation Needed